## Slide 1: White-Rodgers 50M56X-843 Universal Single Stage HSI Integrated Furnace Control for PSC & ECMx Blower Motors
Introduction

## Slide 2: Business and Product Overview

## Slide 3: White-Rodgers Universal Replacement Controls Just Got Better
The White-Rodgers 50M56X-843 Single-Stage PSC & ECMx Control
  Replaces over 550 single-stage controls, making it the most universal single-stage integrated furnace control available. It combines the 50M56U-843 and the 50X57-843 into one control for both PSC & ECMx blower motors!
  This new control now has the major OEM connectors on the board, eliminating the need for a harness. The single microprocessor oversees all furnace functions including burner and blower operations.
  An included 21D64-2 HotRod 120v Universal Ignitor allows for the control to be used to upgrade an existing 80v ignition control.
  Easy configuration and diagnostics with the White-Rodgers Connect app or the digital led display with option and select buttons.

## Slide 4: The 50M56X-843 Streamlines Inventory
    Replaces over 550 part numbers ​
    Configurable for both PSC & ECMx blower motors​
    21D64-2 120v HotRod Ignitor included – required for replacing 80v applications​
    Twinning capable​
    120v humidifier, 24v humidifier and 120v electronic air cleaner connections
    Second-Stage cooling & dehumidification options

## Slide 5: The 50M56X-843 Simplifies Installation & Diagnostics
    NFC technology allows for easy configuration with the White-Rodgers Connect app
    Digital display provides an alternate method to configure and diagnose control​
    Multiple connectors allow for direct plug-in of OEM harnesses​
    Control auto-detects harnesses plugged in​
    Detachable thermostat bus connector for easy wiring ​
    Multiple control mounting options match OEM’s, including tabs to slide in trays with slots​
    Fault code label on control​
    Live real-time flame current readout

## Slide 6: Quick Configuration & Diagnostics with the White-Rodgers Connect App
    App provides simple configuration without power prior to installation
    No login or username required
    Configure with preloaded OEM settings or customize module configurations
    Diagnose fault codes and troubleshoot confidently
    View status and details about the module
Near-field Communication (NFC) creates an interface between the control and your mobile device with the White-Rodgers Connect app. Just place your mobile device on the control to enable a connection.
Once downloaded, the White-Rodgers Connect app does not require cellular/Wi-Fi service to use.

## Slide 7: Onboard Major OEM Connectors
    The 50M56X-843 has five main harness connectors, with both In-line and Molex plugs on the same control
    Four inducer/ignitor Molex connectors on-board
    Two ECMx connectors for Trane & Goodman direct plug-ins
    Direct OEM plug-in allows for a quick installation with multiple OEM brand controls, simplifying the process and eliminating the need for harness adapters
TECH TIP: During initial start-ups, the control will perform an auto-configuration sequence that takes approximately 30 seconds
Inducer/Ignitor Connectors
Main Harness Connectors
ECMx Connectors

## Slide 8: Comprehensive Cross Reference & Product Information
Find the right part while on the job.
  Your on-the-go resource for:
  Complete cross reference
  Product information and spec sheets
  Installation information and videos
  Wiring diagrams
  Select product by features
  Priority technical support
  WR Mobile App Search for “WR Mobile” in both Apple and Google Play Stores
  Desktop Version Access the online version HERE
Search by OEM, Competitor and White-Rodgers part numbers.

## Slide 9: Technical Overview

## Slide 10: What’s in the Box
List of Contents:
    50M56X-843 Control
    21D64-2 HotRod Ignitor
    4 ½" Self-Tapping Screws
    5 Mounting Standoffs
    6 3/16" Female Spade Terminals
    6 1/4" Female Spade Terminals
    Installation Instruction Sheet
1-Year Warranty

## Slide 11: White-Rodgers 50M56X-843 Components
    3/16 Blower Neutral Spade
    6 Line Neutral Spades
    Transformer Neutral Spade
    Line Input Neutral Spade
    4 120v Inducer/Ignitor Molex Harness Plug-ins
    Line 120v Input Spade
    120v Transformer Spade
    120v ECMx Blower Spade
    120v Humidifier Spade
    120v Inducer Spade
    120v Ignitor Spade
    120v EAC Spade
    2 Blower Park Spades
    PSC Blower Heat Spade
    PSC Blower Cool Spade
    PSC Blower Fan Only Spade
    2 24v ECMx Inline Harness Plug-ins
    24v ECMx Blower Speed Spades
    24v ECMx Blower Common Spade
    24v ECMx Blower Trane Common Spade
    Both 3/16” & ¼” 24v Transformer Input Spades
    5a Low-Voltage Fuse
    Twinning Spade
    5 24v Inline/Molex Main Harness Connectors
    24v Humidifier Spade
    24v Removable Thermostat Bus
120V Components:
24V Components:
22
7
19
23
17
18
20
19
23
27
28
28
29
32
33
30
31
16
15
14
13
12
11
10
9
8
7
6
5
4
1
3
2
24
25
26
21
    Flame Sense Test Pins
    1x 3/16" Spade & 1x 1/4" Spade
    Mounting Holes
    Ignition & Blower DIP Switches
    Option & Select Buttons
    Digital LED Readout
    Future Accessory Connector
Other Components:

## Slide 12: White-Rodgers Controls with NFC
Burner Area
Blower Area
    Configuration only controls burner area settings
  The White-Rodgers 50D50U-843 24v Spark Ignition Module was designed to control the burner area only. The universal control settings that are adjustable deal with the burner section of a furnace only:
    Trial for ignition sequence
    Inducer purge timings
    Flame sense type
    Configuration primarily controls blower area settings
  The White-Rodgers 50M56X-843 Integrated Furnace Control was designed to control the blower area settings:
    Blower motor type
    Blower time delay settings
    Inducer purge timings
Burner Area Modules
Integrated Furnace Controls
Notes: 77777 -=`+36* q q

## Slide 13: Two Ways to Configure and Diagnose
The Upgraded Design Now Has On-board Programming That Allows for Configuration
Use the White-Rodgers Connect App and Do All the Programming From Your Smartphone
The White-Rodgers Connect app offers the fastest, easiest configuration setup ever!

## Slide 14: Quick Configuration & Diagnostics with the White-Rodgers Connect App
Download
Scan
    App provides simple configuration without power prior to installation
    Configure with preloaded OEM settings or customize module configurations
    Diagnose fault codes and troubleshoot confidently
    View status and details about the module
Download
    Go to your app store
    Type in WR Connect
    Install the app
Easy Configuration
No Username Or Log-in Required
TECH TIP: White-Rodgers Connect app for HVAC replacement control configuration & diagnostics is an industry first!
Connect

## Slide 15: White-Rodgers Connect App Simplifies Configuration and Diagnostics
    Type the replacement part number into the Configuration tab of the White-Rodgers Connect app to automatically configure the 50M56X-843 universal control to the original default settings for the replacement part number.
    This can be completed without power to the control and before installation.
Intermittent Pilot Setting
Enter replacement part number to automatically configure the All-Spark.

## Slide 16: Fully Customizable Configuration Programming in App
    Blower Type
      Select between PSC & ECMx blowers with multiple speed options
    Blower Timings
      Adjust blower heat on & off time
      Adjust blower cool on & off time
      Adjust blower fan on & off time
    Inducer Purge Timings
      Comes set at default for most cross-reference SKU’s. Available for timing adjustments if needed.
Both ignition and blower options are shown in the 50M56X-843 Configuration Settings
Quick Configuration Setup!
Configuration

## Slide 17: Update Configuration Settings from the App
    After making configuration changes, tap “Update Control” and hold your smartphone over the module again
    Once the new configuration is uploaded, a confirmation will display
    The settings for the control have been updated. You can then share a .txt file via an email or by texting. This .txt file can be printed or stored electronically in a customer's records at the installation company’s office.
White-Rodgers Connect
Easy to Update
Tap
Update
Share
It takes 5± seconds to update when holding your phone steady over the module.

## Slide 18: Additional App Features
Status
    See what is going on with voltage, configuration and operation
Diagnostics
    Look up current active errors as well as the last five errors that have occurred is the last 14 days
    View troubleshooting tips
About
    Get module-specific information, including the date code and the operating firmware
The app displays all the information shown on the 7-segment display and more!
Tap
Only White-Rodgers gives you all this info on your smartphone!
Status
Diagnostics
About

## Slide 19: Understanding NFC App Configuration
The control can be powered up to read or update the control, but does not have to be.
If you know the configuration settings ahead of time, they can be uploaded into the 50M56X-843 before leaving the shop.
Making changes in the app does not require the mobile device being kept on the control.
Once the control is read, the device can be moved away and easily held to make configuration changes or read control information.
No phone service or data connection is required when communicating.
To read, hold the mobile device on the NFC icon for a few seconds until a confirmation check mark appears.
After making changes in the White-Rodgers Connect app, users then must tap the “Update Control” button and hold the device on the NFC icon for up to ±5 seconds while the data packets upload.

## Slide 20: Three Easy-to-Install Mounting Options
  4 ½" self-tapping screws are supplied for multiple mounting options.
  Utilize existing slots by using slide-in tabs molded into the tray.
  White-Rodgers’ molded tray base provides space between the board and the unit mounting plate. Five standoffs are included for snap-in mounting.
Seven Mounting Tabs
Five Standoff Holes
Two-slot Slide-in Tabs

## Slide 21: Twinning Feature
    Two 50M56X-843 controls can be connected to operate simultaneously.
    Twinning requires a connection of the twin terminal on both boards using an 18ga wire.
    The board with the thermostat connection will fully function, including the LED indicator and DIP switch settings. The twinned board will operate simultaneously as determined by the wired board unless “W” or “Y” are powered to it.

## Slide 22: Easy On-board Setup Configuration
    After the system is powered on, the display will read ON when in standby mode. To enter setup, press the “Option” button.
    Refer to the installation instructions on page 2 for details on how to navigate the "Option" and "Select" buttons.
  Match blower timer settings to the old control being replaced.
Configure Using the Option & Select Buttons

## Slide 23: Universal Applications
  80V ignition systems that must be upgraded to 120V by replacing the OEM ignitor with the included HotRodTM ignitor. See the installation instructions on page 5 or verify with WR Mobile for cross-reference numbers that apply.
  When replacing a failed Resideo/Honeywell H9200U1000, ICM ICM2812-KIT & ICM-2812, or White-Rodgers 50M56U-843 & 50X57-843, identify and remove any wiring adapter harness between OEM furnace wiring and the failed universal control prior to installing a 50M56X-843.
  With the 50M56X-843 able to replace both PSC & ECMx blowers, configuration must be set to the type of motor as well as the quantity of speeds.
  The Configuration Menu setting #6 (bLr) must be set to match the equipment's blower.
80V Ignitor Controls
Blower Type Selection
Replacing Existing Universal Controls

## Slide 24: Special Case Applications
Goodman Hybrid 2-Stage
OEM Wiring Connectors
Roll-Out Configuration
Flame Sensor Kit
A unique system known as the “Goodman Hybrid” system is a furnace with a two-stage gas valve paired with a single-speed inducer motor and a single stage blower.
50M56X-843 is able to operate these unique applications with the following cross-reference controls:
Certain Trane, American Standard, and York (including York P3UR/PCLU) furnaces do not have an individually monitored rollout switch in their main harness wiring configuration.
No shunt or jumper is now required.
The Configuration Menu setting #21 (rOb) to (yES) will digitally bypass the rollout input.
Some OEM furnaces, for example Trane and American Standard have a plastic connector housing that groups together line and neutral spade terminals.
When found, remove the block and install the supplied quick-connect spade terminals.
If the 1994 or earlier Rheem/Ruud control being replaced has two green lights (no amber light) and a date code of 3294 or earlier, a Flame Sensor Kit, RHEEM part number 62-24044-71, required (not available through White-Rodgers).
Goodman Controls | 
PCB00109 | PCBBF109
PCBBF109S | PCBBF122
PCBBF122S | PCBBF132
PCBF132S | 

## Slide 25: Get Flame Current Reading Without Meter
  During a call for heat when a flame is present, the digital display will display the flame sense in Microamps.
  No more needing to pull out a meter to get a Microamp reading–just look at the display!
  Standard Test Pins Also Available
  Two pins can be found on the right edge of the control board.
NEW On-Board Read-out

## Slide 26: Thermostat Wiring Made Easy
    Connect thermostat wiring away from the board
    No more getting into the furnace to get the wiring connected–just connect it out front, verify wires are secure in the block, then plug in!
    When the dehumidification terminal on the block is used, the control will slow the blower down during cooling for increased humidity removal.
Lift-off Thermostat Connector Block, Including Dehumidification

## Slide 27: Onboard Status & Fault Codes for Troubleshooting
    Easy-to-see digital display shows fault/error conditions
    Troubleshooting is simplified with a fault code/status label on the control cover
The Option & Select Buttons Allow For:
    Menu configuration
    Recall of the last five faults
    Fault code erasure
1
2

## Slide 28: Universal Integrated Furnace Controls Competitive Comparison
Feature | Resideo / Honeywell S9200u1000 | Icm Icm2812-kit | White-rodgers 50m56x-843
Stages / Blower Types | 1 - PSC Only | 1 - PSC Only | 1 - PSC & Ecmx
Mobile App, NFC, BLE* | No | No | Yes – WR Connect
Harnesses | 8 | 11 | None – OEM Harness Detected
Cross-references | 200+ | 150+ | 550+
Ignitor Voltage Serviced | 120V Only | 120V Only | 80v & 120v
Includes Universal Ignitor | No | No | Yes
Configuration Options | Limited - 4 Dipswitches | Limited - 2 Dipswitches | Unlimited App Or Push Buttons
LED Displays | Tri-color LED Light | Red LED Light | Digital LED Display
Rollout Accessory | Difficult Wire Jumper | Difficult Wire Jumper | Not Required
Flame Current Test | No | No | Digital Readout Or Test Pins
Full Cover W/ Fault Code Label | No - Tray Only | Yes | Yes
Fault Recall & Clearing | Jump R & D Terminals | Push Button | WR App / Push Buttons
Status & Diagnostics | Count LED Flashes | Count LED Flashes | Read On Display Or App
Humidifier Output | 120V Only | 120V Only | 24V Or 120V
2nd Stage Cooling & Dehumidification | No | No | Yes
White-Rodgers Has More Features

## Slide 29: 50M56X-843 Benefit Summary
  Say goodbye to a bundle of harnesses!
  With harness auto detection, no adapter harnesses are needed to connect a furnace to the 50M56X-843!
  Near-field communication controls can quickly and easily be configured in the palm of your hand and directly uploaded into the control.
  Diagnostics can be seen at a glance!
  No more manually going through manual DIP switches.
  Using the WR Connect app or the on-board three-digit, seven-segment digital display, all settings can be quickly accessed.
Auto Harness Detection
Fast Configuration
NFC Setup & Diagnostics

## Slide 30: Installation Overview

## Slide 31: Disconnect Power and Gas
  First, ensure power and gas are disconnected prior to servicing the unit.
1

## Slide 32: Check the Part Number on the Existing Control
  Check the part number on the existing control and verify it is one of the more than 550 modules that can be replaced with the 50M56X-843.
2

## Slide 33: Take a Picture of Wiring
  Take a picture of the existing module for reference before removing any wires.
3

## Slide 34: Disconnect the Thermostat Wiring
  Disconnect the thermostat wiring. Take note of what color wires are going to each terminal. Continue removing the rest of the wires in groups.
4

## Slide 35: Remove the Board
  Remove the board by unscrewing any screws and disconnecting any standoffs holding the board in place.
5

## Slide 36: Configure the Board
  On-board configuration can be done after the board has been installed and powered up.
  Mobile app configuration is the preferred method, and can be done prior to installing the control.
6

## Slide 37: Mobile App Configuration – Download the App
  Use the QR code on the product label to download the White-Rodgers Connect app.
6

## Slide 38: Mobile App Configuration – Connect to Control
    Open the app and tap on “Connect to Control”.
    Place the mobile device in contact with the NFC logo on the control.
    A check mark will appear showing the connection was successful.
    The app will then display the 50M56X-843’s configuration screen.
7

## Slide 39: Mobile App Configuration – Adjust Settings
    Auto-set: enter replacement part number to configure to preloaded OEM settings
    Settings can be adjusted to match the existing control
    Additional configuration options may pertain to your specific application
    Reference the instruction manual for a complete list of configuration options
8

## Slide 40: Mobile App Configuration – Upload to Control
    Select “Update Control”
    Hold the mobile device near the NFC logo
    A check mark will display showing the update was successful
9

## Slide 41: Mounting Options
  The control has seven mounting tabs, five standoff holes and two slide-ins.
10

## Slide 42: Mount the Control
  Use the mounting that matches the existing control, if possible.
  Make sure you don’t damage any components, such as wire harnesses or blower wheels, when drilling or installing screws.
11

## Slide 43: Wiring the New Board
    Identify the main connector on the OEM wiring harness
    Attach it to the matching connector on the new control. Attach the 11-pin connector.
    Use the wiring diagrams in the installation instructions for proper OEM connector and wire identification
12

## Slide 44: Wiring the New Board
  For six-pin ECMx applications, identify the correct connector on the control and plug in the ECMx motor harness.
  For ECMx spade terminal applications, plug the motor wires on the matching terminals.
13

## Slide 45: Wiring the New Board–Special Case Application
  For OEM wiring using a plastic connector to group together 112V power and neutral terminals, cut the wires near the housing and install the supplied quarter–inch quick–connect spade connectors.
14

## Slide 46: Wiring the New Board – Special Case Application
  The three 120V line wires can be connected to the Line H, transformer H and C I R C, in any order.
  Connect the three neutral wires to the Line N, Transformer N and Neutral 1 terminals.
15

## Slide 47: Wiring the New Board – Most Applications
  Connect the individual wires to the new control board.
  Connect the line-in 120V power and transformer wires. Then connect the 120V neutral and transformer neutral wires.
16

## Slide 48: Wiring the New Board – Most Applications
  Plug in the two wire Molex plug for the inducer and ignitor. Connect the PSC blower wires: heat, cool, park and neutral.
  Identify the correct spade size for the 24V hot and common wires and attach the transformer low-voltage wires to the correct terminals.
17

## Slide 49: Wiring the New Board – Most Applications
  Remove the thermostat bus block from the control and install the thermostat wires according to the terminals they were removed from.
  Then plug the block back into the control.
18

## Slide 50: Check the Ignitor
  If the control being replaced operated an 80V ignitor, the existing ignitor must be replaced with the included Hot Rod ignitor.
  For all other applications, inspect the existing 120V ignitor to determine if it must be replaced.
19

## Slide 51: Ready to Test – Reconnect Power and Gas
  Reconnect the electric power and gas to the unit
  Make sure the door switch is engaged
  .
20

## Slide 52: Automatic Harness Configuration
    The 50M56X-843 automatically configures the control to match the harnesses that have been attached
    The process takes up to 30 seconds at first power-up
    After two consecutive matching power-ups, the control will write the configuration in memory
    See the installation instructions if the control needs to be reset for a different application
21

## Slide 53: Self-Test Mode
  “Self-test” mode allows the control to test most furnace components without requiring a call for heat.
  To enter the self-test mode, go into the configuration settings and choose “YES” on option number 22.
22

## Slide 54: Self-Testing
  The system first tests the inducer, then tests the igniter to make sure that it is wired and connected correctly.
  During an active call for heat, cool or constant fan, the LED display will alternate between up to three status indicators.
23

## Slide 55: Make a Call for Heat
  When you make a call for heat the control will show “Heat” mode.
  The inducer will start and the control will show that is in the heat mode and is doing a pre-purge with the inducer.
  The furnace will go through a 30-second pre-purge first. Then after that we will start our trial for ignition.
24

## Slide 56: Verify Proper Ignition
  The trial for ignition will show ignition on the LED. When lit, a signal is sent through the flame sense probe to indicate that ignition has occurred.
  In heat mode, the display will rotate through several different display readings, including heat and then C and a number, indicating that the flame probe is sensing those Microamps in the circuit.
25

## Slide 57: Active Error
  If incurred, the active error will show on the display. The error can be referenced on the label so you know exactly what to look for when an error occurs from the control display.
26

## Slide 58: Finalize Tests
  Finalize any tests you would like to complete.
  Terminate the call for heat.
27

## Slide 59: Fault Code Errors: On Furnace Control
  Fault code errors can be recalled through the White-Rodgers Connect mobile app or onboard the equipment.
  Press "Option" and "Select" buttons for two to five seconds to find a fault that has been stored. The unit will show any errors that have occurred.
  To clear any fault codes, press and hold the, "Option" and "Select" button together for five to ten seconds until the display will read, ”clear faults."
  The history will be cleared out of the control. If a fault occurs, it naturally clears after 14 days.
28

## Slide 60: Fault Code Errors: WR Connect
  Open the app and select the “Connect to Control” button. Place the mobile device near the NFC logo on the module and wait until a check mark appears showing the connection was successful.
  The app will then display the module’s settings configuration page. To see any errors, select the Diagnostics tab. Errors will be listed with the most current at the top.
29

## Slide 61: Fault Code Errors
  For detailed information and troubleshooting tips, select the arrow by the fault.
30

## Slide 62: Fault Code Errors
  To clear errors in the app, tap the "Clear Error History" button.
  Place the device in contact with the NFC logo on the module and wait for the check mark to appear.
  This action can be performed whether the module is powered on or powered off.
31

## Slide 63: Details of This Control
  Click the About tab to get details about the control and customer service information.
32

## Slide 64
Thank you.
R-5648. ©2024 Copeland LP.