## Slide 1
50E47U-843 Universal Hot Surface Ignition Module
Product Training

## Slide 2: Product and Business Overview

## Slide 3
Universal Hot Surface Ignition Module
50E47U-843
3
White-Rodgers Connect App
50E47U-843
Universal Hot Surface Ignition Module
NEW
Replace over 325 HSI module part numbers that use 24V, 120V, or 240V ignitors
Simplify configuration and diagnostics with the White-Rodgers Connect App
Convert old board wiring effortlessly with the easy-install harness
Setting the standard in universal parts for HSI applications

## Slide 4
A Non-Integrated Control is a partial control that connects to another for complete operation.
For forced-air units, the 50E47U-843 will integrate with a 50F06-843 Fan Timer module to complete the furnace operation.
Installation videos are available for both controls.
What is “Non-Integrated”?
Non-Integrated Furnace Application
50E47U-843
Universal Hot Surface Ignition Module
50F06-843 White-Rodgers Universal Furnace Electronic Fan Timer
+

## Slide 5
Replaces over 325+ HSI module part numbers for multiple applications that use 24v, 120v, or 240v ignitors.
Controls an inducer motor and monitors a pressure switch when needed.
Streamline Inventory with Multiple Brand Cross-references
Honeywell S8910U3009
ICM283
Robertshaw HS780
Fenwal 35-65, 35-66
UTEC 1018 series
White-Rodgers 50E47-843
Carry less inventory and have the right part on the truck to service multiple HSI applications

## Slide 6
Multiple Applications
Stand-alone applications still being manufactured
Infrared Heater
Pool Heaters
Cooking Equipment
Water Heaters
Gas Boiler
Unit Heaters
Gas Furnace
Laundry Equipment
Most common application
Pool heaters
Water heaters
Unit heaters
Gas furnaces
Boilers
Cooking equipment
Laundry equipment
Infrared heaters

## Slide 7
Quick Configuration & Diagnostics with the White-Rodgers Connect App
Near-field Communication (NFC) creates an interface between the control and your mobile device with the White-Rodgers Connect app. Just place your mobile device on the control to enable a connection.
Once downloaded, the White-Rodgers Connect app does not require cellular/Wi-Fi service to use.
App provides simple configuration without power prior to installation.
No login or username required.
Configure with preloaded OEM settings or customize module configurations.
Diagnose fault codes and troubleshoot confidently.
View status and details about the module.
No more setting dipswitches or counting flashing LEDs

## Slide 8
The White-Rodgers Connect app simplifies configuration and diagnostics for the ignition module.
Type the replacement part number into the configuration tab of the White-Rodgers Connect app to automatically configure the ignition module to the original default settings for the replacement part number.
This can be completed without power to the control and before installation.
Configure quickly and accurately with auto-set
White-Rodgers Connect Auto-set Feature
Take the guesswork out of configuration
Enter replacement part number to automatically configure the module.

## Slide 9
By providing a harness with ¼” spade connectors, all the wiring can be removed one at a time from the existing control and matched up with the harness labels prior to removing the existing control.
The harness can then be plugged into the new HSI module.
For some applications six 3/16” spade connectors are provided.
Control Voltage Wiring Simplified
24v 11-Pin Wiring Harness
Allows low-voltage wire transfer before removing the existing control to prevent install errors

## Slide 10
Setup operation timings and features using the Option and Select Buttons.
3-Digit Digital Display
Status
Diagnose
Provides alternate method for configuration, status and diagnostics
Configure
Active error codes are displayed and referenced on product label. Stored error codes can be accessed and cleared using buttons.
Real-time operation status and flame current is displayed.

## Slide 11
The White-Rodgers 50E47U-843 Universal Hot Surface Ignition Module can act as a thermostat and turn the module on and off. By connecting the F67-8535 Temperature Sensor to the 50E47U-843, the digital display can be used to show a temperature setting is adjustable using the “Option” & “Select” buttons.
The Integrated Thermostat feature is designed for infrared & tube heaters that are installed in the area they heat. It can maintain a specific temperature without the system being manually turned on & off or having a separate thermostat installed.
Plug-in temperature sensor
Function can be turned on/off in programming
Easy temperature adjustment
Display current Setpoint
Display set temperature
Adjustable from 40°F to 80°F
The White-Rodgers F67-8535 Plug-in Temperature Sensor
Features
Introducing the Integrated Thermostat Sensor
F67-8535
Easy to Install, Easy to Configure, Easy to Operate
Maintain temperature without the need for an external thermostat

## Slide 12
Applications that control the temperature of the space they are in can now be fully controlled at the Unit. By utilizing the HSI module 50E47U-843 with a F67-8535 Temperature Sensor attached, the thermostat feature allows for a complete self-contained functioning system!
NOT INTENDED FOR FURNACES.
Fully Independent
Integrated Thermostat Applications
Space Heater
Infrared Heater
Tube Heater
+

## Slide 13
The 50E47U-843 Universal HSI Module works with 24v, 120v, or 240v input power.
The Universal HSI Module
Jumper for Local vs Remote Flame Sense
Tall Flame Sense Test Pins
Inducer Relay
Power In/Power Out to Hot Surface Ignitor
Pressure Switch Connection
Special 240v Application
3 Digit 7-Segment LED Display
NFC Capability and App Included
11-pin In-line Connector for Easy 24v Wiring
Low Voltage Fuse

## Slide 14
New 50E47U-843 Features Differentiate Product from Competition Across The Board
50E47U-843 Feature Comparison
Options | Fenwal 35-65, 66 | Robertshaw 780-787 | ICM 283 | Honeywell/Resideo S8910U | (current) White-Rodgers 50E47-843 | (New) White-Rodgers 50E47U-843
Flame Sense Type | Either/Or | Remote | Both | Both | Both | Both
Gas Valve Contact Rating | 2A | 1.5 | 1.5 | 2A | 1.5A | 2A
Control Voltage | 24V 50/60Hz | 24V 60Hz | 24V 60Hz | 24V 60Hz | 24V 60Hz | 24V 50/60Hz
Ignitor Voltage | 24/120/240V | 120V | 120V | 120V | 120V | 24/120/240V
Inducer/PSW | Yes | No | No | No | No | Yes
Mobile App | No | No | No | No | No | WR Connect
Configuration | None | None | Dipswitches | Dipswitches | Keys | App or Push Buttons
Display | Single LED Bulb | None | Single LED Bulb | Single LED Bulb | Single LED Bulb | 3 Digit 7-Segment
Diagnostics | Count LED Flashes | None | Count LED Flashes | Count LED Flashes | Count LED Flashes | Read on display or app
Flame Current Test | No | No | No | Test pads | No | Digital Readout or Test Pins
Integrated Thermostat | No | No | No | No | No | Yes
By Being Able to Replace Fenwal Series, the 50E47U-843 is the most Universal HSI Control Available with Premium Connectivity Option

## Slide 15
The 50E47U-843 allows for 24v, 120v, and 240v Input voltage in one Universal Module
New additional connections like the 120v ignitor terminal for 24v applications add to cover more options.
The 24v 11-pin Harness has all configuration wires that are made active through personalized configuration.
By plugging wires 1st into the harness, all low voltage wiring can be completed prior to the existing module being removed.
The onboard digital display shows real-time flame current during the heat operation, so there’s no need to pull out your meter to check for a good signal.
Speed up your operation check and know your leaving the unit in good shape!
3 Voltages in 1
Flame Sense Displayed
Easy Connections
Utilizing Near Field Communication, the 50E47U-843 can be easily configured in the palm of your hand and directly uploaded into the control.
The convenience of the NFC feature is the Icing on the Cake!
Mobile Configuration
Features of 50E47U-843
Summary

## Slide 16
Search by OEM, competitive, or White-Rodgers model number
Try the desktop version at https://wrcrossref.com
Your resource for:
Complete Cross Reference
Product information and spec sheets
OEM compatibility
Installation information and videos
Wiring diagrams
Priority technical help
Always up-to-date and easy to use
WR Mobile App
Scan the QR code to download from your app store.
Search
Scrollable Product List
White-Rodgers Replacement

## Slide 17: Technical Overview

## Slide 18
List of Contents:
What’s in the Box
50M47U-843 Module
11-pin 24v Harness
Flame Sense Jumper (factory installed)
4 - 1” mounting Screws
6 - 3/16” Male Quick Connect Spade Terminals
2 - 14-16 AWG ¼” Female Quick Connect Spade Terminals
Instruction Sheet with QR Code link to Installation Resources and QR Code for White-Rodgers Connect App

## Slide 19
F67-8535 Integrated Thermostat Sensor
Installation Instructions
¼” Female QC Spade Terminal
List of Contents:
What’s in the Box: F67-8535
SOLD SEPERATELY

## Slide 20
White-Rodgers 50E47U-843 Components
11-pin In-line Wiring Connector
Low Voltage Fuse
HSI L1 120v Output Spade for 240v Applications
Line Voltage L1 120v Input Spade for 240v Applications
Line Voltage L2 120v Common Input Spade for 240v Applications
HSI L2 120v Common Output Spade for 240v Applications
24v Components:
5
3
7
1
2
3
4
5
6

## Slide 21
120v Inducer Input and Output Spades
HSI 120v Output Spade for 240v Applications
HSI L1 120v Output Spade for 240v Applications
Line Voltage L1 120v Input Spade for 240v Applications
Line Voltage L2 120v Neutral Input Spade for 240v Applications
HSI L2 120v Neutral Output Spade for 240v Applications
120v Components:
White-Rodgers 50E47U-843 Components
5
3
7
7
8
9
10
11
12

## Slide 22
White-Rodgers 50E47U-843 Components
HSI 120v Output Spade for 240v Applications
HSI L1 120v Output Spade for 240v Applications
Line Voltage L1 120v Input Spade for 240v Applications
Line Voltage L2 120v Input Spade for 240v Applications
HSI L2 120v Output Spade for 240v Applications
240v Components:
5
3
7
13
14
15
16
17

## Slide 23
Flame Sense Jump Spade
Flame Sense Spade
S8910 or 35-65 Mounting options
Flame Sense Test Pins
Remote Thermostat Sensor Connection
Near Field Communication Connect Area
Digital Status / Fault LEDs
Options/Select Buttons
Other Components
White-Rodgers 50E47U-843 Components
5
3
7
18
19
20
21
22
23
24
25

## Slide 24
Flame sense can be configured to sense the flame through the “Local” spark rod or “Remote” through a separate flame sensor.
A REMOTE configuration refers to using 2 separate circuits for the Hot Surface Ignitor and flame sense circuits to operate independently
A LOCAL configuration refers to using a Hot Surface Ignitor for both ignition and flame sense in one wire
Local vs Remote
Local
Remote
Flame Sense Jumper Feature
Use Jumper
or
Use Sense/S1 Spade
For Remote application simply remove the jumper.

## Slide 25
During a call for heat when a flame is present, the digital display will display the flame sense in Microamps.
The display will flash between “Ht”, indicating the system is in the heat mode, and “C” followed by 2 numbers indicating the real-time flame current!
2 pins extend from the Control Board to the surface of the Cover.
TO TEST:
The Furnace must have a call for heat and the burners producing flame.
Set a multimeter to vDC and place a meter probe on each pin.
Convert vDc to MicroAmps using a 1:1 ratio.
A good flame sense reading will be between 1.0 – 5.0 μA.
On-Board Display
Flame Test Pins
Flame Current Reading Features
2 Ways to Get Flame Sense Reading
Test Pins

## Slide 26
Whatever voltage is applied to L1 and L2 on the Control will come out HSI1-120 and HSI2-FS.
For applications that supply voltage input is 240v and the Hot Surface Ignitor is 120v, use output terminals HSI-240 and HSI2-FS
When replacing controls that internally power the inducer motor from L1, a field created jumper from L1 to F1 may be required.
HSI Applications
HSI and Inducer Motor Connections
Understanding Line Voltage Connections
Power in
Line voltage does not power up the control. That is done through 24v or Th-W on the 24v 11-pin harness.

## Slide 27
When the module is used in inducer applications, the pressure switch circuit monitors the exhaust, and the inducer relay operated the inducer motor.
The 50E47U-843 has both Pressure Switch In (PSI) and Pressure Switch Out (PSO) terminals.
The module will not allow for system ignition until a signal is present on pressure switch circuit indicating the switch has closed.
Inducer Applications
Inducer and Pressure Switch Options

## Slide 28
By providing a harness with ¼” spade connectors, all the wiring can be removed one at a time from the existing control and matched up with the harness labels prior to removing the existing control.
For some applications six 3/16” spade connectors are provided.
Control Voltage Wiring Simplified
24v 11-Pin Harness
Allows low-voltage wire transfer before removing the existing control to prevent errors
Wires are identified and placed differently on the 50E47U-843 and 50D50U-843. The 11 pin in-line harnesses cannot be swapped using the identifier tags.

## Slide 29
By connecting a F67-8535 Thermostat Sensor, the 50E47U-843 will be able to function as its own thermostat and maintain a temperature set on the seven-segment display.
Hardware Expansion Port
Future accessory connector
Integrated Thermostat Sensor
Additional Features
SOLD SEPERATELY

## Slide 30: Integrated Thermostat Feature
Disconnect electric power.
Make all needed connections for the 11-pin harness and line voltage wiring.
Connect a White-Rodgers F67-8535 temperature sensor into the “AirT” port.
Connect the System Safety circuit using the “R” and “TH-W” connections.
Using the White-Rodgers Connect app, connect to the module and go tap the configuration tab or enter into the onboard programming mode during initial power-up.
Program the control and turn on the integrated thermostat feature.
Power up and test.
Installation
White-Rodgers
F67-8535 Temperature Sensor
R (OUT)
TH-W
AirT
Safety
4
5
Additional integrated thermostat options are available in the installation instructions.
2
4
3
2
2
5
6
5
6

## Slide 31
4 mounting holes are designed to match the board being replaced and give multiple options for alternate mounting.
4x ¼”x1 Mounting screws are provided.
Matches Modules being Replaced
Mounting Options
The is a sub-header right here
White-Rodgers matches mounting holes with most common competitors' modules.

## Slide 32
Configure the Universal HSI module on your smartphone.
Download the App from your play store
Go to your app store
Type in White-Rodgers Connect
Install the App
Set up your control faster.
Using The White-Rodgers Connect App
Easy configuration and diagnostics
Configure | Diagnose | Troubleshoot from your smartphone.
32
Download and Connect
Configure
Status
Diagnose
Product Information and Support

## Slide 33
To connect to your NFC enabled control tap,
connect to control. Place the NFC region of your mobile device on the target icon of your White-Rodgers control.
The text in pink shows your control settings. This text will change as you make modifications to each setting. If you tap on the name of a parameter, the app will display a description about each one for some controls.
Keep your device in contact with the target icon until a check mark appears and the app transitions to the configuration tab. You can then move your device away from the control.
NFC
Connecting
Configuring
Once you've chosen your desired settings, tap update control. Place the NFC region of your device on the target icon of your White-Rodgers control, keep your device steady until a checkmark appears.
Updating
Understanding Near-field Communication
White-Rodgers Connect app communicates with the control through NFC
The auto set feature allows you to enter the replacement part number to automatically configure the White-Rodgers control to the replacement parts original settings.

## Slide 34
Configure using the Options and Select Buttons
After the System is powered on, the Display will read ON when in Standby mode. To enter set-up, press the Option Button.
Refer to the Installation Instructions Pg #2 for details on how to navigate the Options/Select buttons.
Utilizing On-Board Configuration
Settings Listed in Installation Table
Configuration Options are found on Table #1 on Pg #3

## Slide 35
During operation, the display will show the status of what is taking place.
See what is occurring in real time.
Status and Error Codes
Refer to the installation instructions page 7 for details on fault codes.

## Slide 36
Watch an in-depth step by step installation and product overview of the White-Rodgers 50E47U-843 Universal Hot Surface Ignition Module, including how to install using the White-Rodgers Connect app.
Installation Overview
WATCH NOW

## Slide 37
White-Rodgers Comprehensive Solutions - Delivered
Industry Leading Products
Used by more OEM’s
Offering the widest range of Universal HVAC parts
Ease of Installation
Simple, easy to understand instructions
Standard wiring nomenclature
Reliability of Product
Quality control provides reliable products
Affordable
Competitive prices
Supported by Knowledgeable Representatives
Contractor direct phone support

## Slide 38: Thank you
R-5796. ©2023 Copeland LP. All rights reserved. | The Copeland and White-Rodgers logos are trademarks and service marks of Copeland LP.