## Slide 1
White-Rodgers
Commercial Rooftop Controls

## Slide 2
Business and Product Overview

## Slide 3: White-Rodgers Commercial Rooftop Controls
As the direct OEM supplier of electromechanical ignition modules for Trane Rooftop Units (RTUs), White-Rodgers is uniquely suited to supply the replacement market, with three unique models and one accessory.
Features
Easy to Install
Full Color Boxes
Complete Cross Reference on Box
Instruction Sheet
Fault Code Label, Accessory Parts to Meet or Exceed OEM Offering
F50N02-820
Accessory Adaptor Board and Harnesses for Spark Controls
50N02B-820
(45s Blower Delay)
Direct Spark Ignition
50E70-820
Hot Surface Ignition
50N02A-820
(80s Blower Delay)
Direct Spark Ignition

## Slide 4: Trane RTU Market Data
Trane has a large installed base of RTUs.
  Electromechanical control boards from 1990 – Present
  Communicating control boards from 2002 - Present
White-Rodgers has long been the OEM Supplier for Trane ignition modules
  Started with Fenwal, Texas Instruments
  Moved to majority W-R, one UTEC SKU
ICM and Honeywell do not offer these key parts, giving White-Rodgers near exclusivity in the category

## Slide 5: Applications
Impack™ *
1.5-5 TON
YCY, YCC, YCZ, DCY, DCZ
Spark Ignition
Precedent™
3-10 TON YSC, YHC
Spark Ignition
Voyager™
12.5-25 TON YCD Hot Surface Ignition
F50N02-820
Furnace Adapter Board
50N02A-820
50N02B-820
50E70-820

## Slide 6: 50N02A-820 & 50N02B-820 Spark Ignition Controls
Product Features and Benefits
Plug and play replacement of the OEM.
Built for Impack and Precedent Product Lines
No wire splicing or modifications necessary
“N02A” version has black silkscreen
  80s Blower Delay
“N02B” version has red silkscreen
  45s Blower Delay

## Slide 7: 50N02A-820 / 50N02B-820 What’s in the box?
50N02A-820 / 50N02B-820 spark control
Installation Instructions
Diagnostic Indicator Tag

## Slide 8: F50N02-820 Spark Ignition Adapter Board
Product Features and Benefits
Replaces Trane’s Service KIT06839
Initial production used a Texas Instruments Spark Module with mounting screws
The adapter mounts to the existing screw holes and converts to plastic stand-off mounting
Newer and already converted units will not need the adapter
Wiring harnesses adapt old system wiring to new control board pinouts
Broad availability to purchase
Original TI Control

## Slide 9: F50N02-820 What’s in the box?
0059-4821 Adapter Panel
9 Pin to 9 Pin Wiring Adapter Harness
12 Pin to 9 Pin Wiring Adapter Harness
Diagnostic Indicator Tag
Installation Instruction Sheet

## Slide 10: 50E70-820 Hot Surface Ignition Module
Product Features and Benefits
Replaces Trane’s Service KIT17852 For Voyager™
Initial production used a Fenwal HSI Module with mounting screws before converting to a Texas Instruments standoff mount control
The included adapter mounts to the existing screw holes and converts to plastic stand-off mounting
Wiring adapter connects control to 24VAC transformer when needed
  Newer units will not need an adapter.
  Sequence and timing are the same as the existing board
Original Fenwal Control

## Slide 11: 50E70-820 What’s in the box?
50E70-820 Integrated Furnace Control
24 VAC Wiring Harness (0155-0263)
59-4819 (3AD-2) Adapter Board
3 – Plastic tie wraps
Installation Instructions
Fault code label

## Slide 12: Commercial Rooftop Controls Cross Reference
50N02A-820
Trane | White-Rodgers
CNT03456 | 50N02A-820
CNT03457 | 50N02-495-02
X13650874-01 | 50N02-495-0
X13650873-01 | 
CNT01634 w/ F50N02-820 | 
CNT01669 w/ F50N02-820 | 
CNT02216 w/ F50N02-820 | 
CNT02217 w/ F50N02-820 | 
50N02B-820
50E70-820
Trane | White-Rodgers
CNT05135 | 50N02B-820
CNT03458 | 
D674713P01 | 
X13650875-01 | 
CNT02219 w/ F50N02-820 | 
CNT04912 | 
Trane | White-Rodgers
3HS-1 | 21D70-495-01
3HS-2 Rev A | 21D70-495-02
3HS-2 Rev D | 50E70-820
KIT03308 | 
KIT05137 | 
KIT08282 | 
KIT17852 | 
3SV-2 | 
X13130449-0 | 
X13130453-01 | 
X13130454-01 | 
X13130454-02 | 

## Slide 13: WR Mobile App
Always up-to-date and easy to use:
Mobile App
White-Rodgers Website
Your resource for:
Product information and spec sheets
Complete Cross Reference
OEM compatibility
Installation information and videos
Wiring diagrams
Download:
Go to your app store
Type in WR Mobile
Install the app
OR
Open your camera
Hold it over the QR code
Tap “Open” on the
pop-down
Install the app

## Slide 14: WR Mobile App
Easy to use!
Search by OEM, Competitive, or White-Rodgers Model Number
Scrollable Product List
WR Replacement
Product Number

## Slide 15: White-Rodgers Cross Reference
Go to: www.whiterodgers.com
Hover over Tools & Resources
Click on: White-Rodgers Cross Reference/Product Information
Enter the Model Number or click on: Search Replacement Heating Controls by Major OEM Brand

## Slide 16: Why Contractors Trust White-Rodgers
Industry Leading Products
Used by more OEM’s
Offering the widest range of Universal Replacement Controls
Ease of Installation
Simple, easy to understand instructions
Product Reliability
Quality Control assures reliable products
Affordable
Competitive pricing
Supported by Knowledgeable Representatives
Contractor direct phone support

## Slide 17
Technical

## Slide 18: White-Rodgers Commercial Rooftop Controls
As the direct OEM supplier of electromechanical ignition modules for Trane Rooftop Units (RTUs), White-Rodgers is uniquely suited to supply the replacement market, with three unique models and one accessory.
Features
Easy to Install
Full Color Boxes
Complete Cross Reference on Box
Instruction Sheet
Fault Code Label, Accessory Parts to Meet or Exceed OEM Offering
F50N02-820
Accessory Adaptor Board and Harnesses for Spark Controls
50N02B-820
(45s Blower Delay)
Direct Spark Ignition
50E70-820
Hot Surface Ignition
50N02A-820
(80s Blower Delay)
Direct Spark Ignition

## Slide 19: 50N02A-820 & 50N02B-820 Spark Ignition Modules
Board Components
Thermostat inputs
Safeties & gas components
24VAC input
Spark Output
Hi/Low inducer outputs
LED
1
2
3
4
5
6
TECH TIP: Remember 50N02B-820 has a 45s Cool Off Delay while a 50N02A-820 is 80s

## Slide 20: 50N02A-820 & 50N02B-820 LED Diagnostic Codes
The green LED will indicate a status code as shown in the table below:
Green LED Flash | Code Status / Error Condition
Steady OFF | No Power / Failure / Internal Failure
Steady ON | Normal, no call for heat
Slow Flash Rate | Normal, call for heat
2 Flashes | System Lockout: Failed to detect or sustain flame
3 Flashes | Pressure switch problem detected
4 Flashes | High Limit switch protection device open
5 Flashes | Flame sensed and gas valve not energized or flame sensed and no "W" signal
6 Flashes | Flame Rollout Switch open
7 Flashes | Thermostat mis wired; W1 and W2 swapped

## Slide 21: 50N02A-820 & 50N02B-820 Adjustable Fan Delay
Adjust Heat and Cool Fan Off Delay jumpers as necessary.

## Slide 22: 50E70-820 Hot Surface Ignition Module
Board Components
High voltage inputs
HSI output
Gas valve output
24VAC input
Flame sense test pins
4-pin plug
Edge card connector
LED
3
4
5
6
1
2
7
8
TECH TIP: An “edge card connector" allows the module to slide into the control board.

## Slide 23: 50E70-820 Hot Surface Ignition Module Voyager™ Product Line
Gas Valve
Energized
Air Enters
Air Orifice
Inlet Plate
Fuel and Air
Pre-mixed
Fuel/Air Mixture
Single
Gas
Orifice
Trane Voyager RTU
Burner Assembly
Ignition Module
Heating Details
Premix “Power” Burner, Not Forced or Induced Draft
Negative Pressure Gas Valve
Drum & Tube Heat Exchanger
120VAC Hot Surface Ignitor
1
2
3
50E70-820

## Slide 24: 50E70-820 LED Diagnostic Codes
The green LED will indicate a status code as shown in the table below:
Green LED | Red LED | Code Status / Error Condition
OFF | OFF | Powered with no call for heat
Flashing* | OFF | Call for heat – no fault detected
OFF | Flashing* | No flame signal on try for ignition or flame signal established and lost prior to a lockout condition
ON | Flashing* | Gas valve mis wired or flame signal present at a call for heat
OFF | Flashing* | Internal fault – anytime
NOTE: • Flashing at 50% duty cycle. • At the start of each retry for ignition, the Red LED will flash for 5 seconds along with a flashing Green LED.

## Slide 25: Testing Flame Current
Understanding Test Pins
2 pins extend from the control board to the surface of the black cover.
To Test:
The furnace must have a call for heat and the burners producing flame.
Set a multimeter to vDC and place a meter probe on each pin.
Convert vDc to MicroAmps using a 1:1 ratio.
A good flame sense reading will be between 1.0 – 5.0 μA.
Flame current test pads

## Slide 26
Install

## Slide 27: Disconnect Power and Gas
1
For this installation, 50E70–820 will be used. All wiring should be installed according to local and national electrical codes and ordinances.
NOTE: If the control being replaced is a Sensata Technologies 3HS-1 or 3HS-2, remove old control and skip to step 6.

## Slide 28: Note Location of Edge Card
2
Before removing the old control, note whether the edge card connector slides into the control on the top side or bottom side. If it comes in on the top, skip to step 4.

## Slide 29: Adaptor Board
3
Remove the old control. Position the 59-4819 (3AD-2) Adapter Board so that the text is right side up, then fasten it in place using the holes marked "METAL STANDOFF".

## Slide 30
4
Attach the quick connect end of the 24 VAC Wiring Harness (0115-0263) to the HOT 24 VAC tap of the low voltage transformer.
Connect 24 VAC Wiring Harness

## Slide 31: Standoffs
5
Align the plastic standoffs on the 50E70-820 control with the remaining holes on the 59-4819 (3AD-2) adapter board and gently press on the control until all 4 standoffs snap into place.

## Slide 32
6
Connect the 4-pin plug of the 24 VAC Wiring Harness (0115-0263) to the 50E70-820 control. Reconnect the remainder of the wiring (edge card connector or quick connects).
NOTE: Equipment manufactured after 1/8/1996 do not require the 59-4819 (3AD-2) adapter board or 24 VAC wiring harness (0115-0263)
Finish Connecting 24 VAC Harness

## Slide 33: Reconnect and verify
7
Reconnect the power and gas to the furnace and use test pins to verify a good flame sense reading.
Test:
The furnace must have a call for heat and the burners producing flame.
Set a multimeter to vDC and place a meter probe on each pin.
Convert vDc to MicroAmps using a 1:1 ratio.
A good flame sense reading will be between 1.0 – 5.0 μA.
Flame current test pads

## Slide 34: 50E70-820 LED Diagnostic Codes
The green LED will indicate a status code as shown in the table below:
Green LED | Red LED | Code Status / Error Condition
OFF | OFF | Powered with no call for heat
Flashing* | OFF | Call for heat – no fault detected
OFF | Flashing* | No flame signal on try for ignition or flame signal established and lost prior to a lockout condition
ON | Flashing* | Gas valve mis wired or flame signal present at a call for heat
OFF | Flashing* | Internal fault – anytime
NOTE: • Flashing at 50% duty cycle. • At the start of each retry for ignition, the Red LED will flash for 5 seconds along with a flashing Green LED.