## Slide 1
49M11-843 SureSwitch™ Multi-Volt Contactor

## Slide 2
Business and Product Overview
49M11-843 SureSwitch™ Multi-Volt Contactor

## Slide 3: Introduction
The 49M11-843 SureSwitch™ Multi-Volt Contactor is the next generation single-phase contactor with a microprocessor brain that replaces 24v, 120v, 208v, or 240v coil contactors.
Microprocessor control nearly eliminates contact welding and pitting
Sealed to keep out insects and debris
Protects condensers from brownouts and short cycling
Compatible with single stage residential AC/Heat pumps with PSC fan motors.
Also compatible with refrigeration equipment such as walk-in coolers, refrigeration cases, ice machines, and carbonated beverage machines.

## Slide 4: Additional Features and Benefits
Optical sensor monitors the arc and adjusts timing.
Open design allows for damage from fire ants, other insects.
  Microprocessor operates a short cycle and random startup timer
  Latching relay eliminates contactor chatter and hum
  Vibrant tri-color LED for operations check and troubleshooting
  Lifetime cycle counter for a fuller view into system life
  Compatible up to a 40 FLA rating / 5 Tons
  Coil terminals are separated with taller walls to prevent electrical shorts
Sealed to reduce damage from insects and debris.

## Slide 5: Why is It Better?
Increases system reliability and homeowner peace of mind.
5x Contactor life
5 Year warranty
Universal replacement
Replaces 287+ parts
Multi-Volt Contactor applicable to wider range of applications including AC, heat pump, refrigeration products with 24v, 120v, 208v, & 240v coils.

## Slide 6: Microprocessor Extends Contactor Life
“Zero Cross” contact control switches without damaging current present.
SureSwitch™ Sealed Relay with Optical Sensor plus unique opening and closing algorithms achieve consistent Zero Cross Switching. Contact shows no damage after 1M cycles.
SureSwitch™
Traditional contactors do not have microprocessor intelligence. They open and close at random, often in the “Arc Zone where damage occurs. Damage shown after 300K cycles.
Traditional Contactors

## Slide 7: Competitive Comparison
Other “sealed contactors” do not offer protection against insect intrusion.
“Arc Cover,” “Dust Cover,” or “Plastic Noise Shields” do not offer the same level of protection as the fully sealed SureSwitch™.
Our contactor housing design limits dust and other contaminants from the magnet structure, reducing noise, eliminating insects, and reducing contactor failure.
No protection.
Some protection but some ants still get in.
Completely sealed
from insects and debris.

## Slide 8: Testimonials
“The SureSwitch, which I installed myself, has actually made my old system run smoother and quieter, it starts up more gentle, and it keeps the bugs from frying it since it's sealed (an issue I've had more than once).”
-Peter
“They seem to me they are superior than a traditional contactor...I was a skeptic at first but I have them on several 10seer 5ton units that would burn up these crappy contactors we have. So far they have held up 2.5 years on my test units.”
-Joe Schearer
“Before I bought this I was replacing my contactor relay at least once a year. It's been 2 years since I installed this and so far so good. It really does start a/c quieter overall.”
-J Shea

## Slide 9: WR Mobile App
Always up-to-date and easy to use:
Mobile App
White-Rodgers Website
Your resource for:
Product information and spec sheets
Complete Cross Reference
OEM compatibility
Installation information and videos
Wiring diagrams
Download:
Go to your app store
Type in WR Mobile
Install the app
OR
Open your camera
Hold it over the QR code
Tap “Open” on the
pop-down
Install the app

## Slide 10: WR Mobile App
Easy to use!
Search by OEM, Competitive, or White-Rodgers Model Number
Scrollable Product List
WR Replacement
Product Number

## Slide 11: White-Rodgers Cross Reference
Go to: www.whiterodgers.com
Hover over Tools & Resources
Click on: White-Rodgers Cross Reference/Product Information
Enter the Model Number or click on: Search Replacement Heating Controls by Major OEM Brand

## Slide 12: Wholesale Resource Site
Access useful resources to grow your business.
Visit: https://climate.emerson.com/en-us/brands/white-rodgers/white-rodgers-wholesaler-resource-center
You’ll find videos, stocking lists and product launch information for the following product families:
Heating Controls
Cooling Controls
Sensi Smart™ Thermostats
Traditional Thermostats
Contractor Rewards
Product Merchandising

## Slide 13: Why Contractors Trust White-Rodgers
Industry Leading Products
Used by more OEM’s
Offering the widest range of Universal Replacement Controls
Ease of Installation
Simple, easy to understand instructions
Product Reliability
Quality Control assures reliable products
Affordable
Competitive pricing
Supported by Knowledgeable Representatives
Contractor direct phone support

## Slide 14: Customer Driven Packaging
1. Universal or Direct OEM
2. Product Type & Color Code
  Red = Indoor Units
  Purple = Outdoor Units
  Gold = Commercial
3. Model Number
4. Large Product Image(s)
5. Key Attributes
  Stages
  Blower Motor Type
  Ignitor Voltage
  Other
6. Cross Reference on box
1
2
3
4
5
6

## Slide 15
Technical
49M11-843 SureSwitch™ Multi-Volt Contactor

## Slide 16: Introduction
The 49M11-843 SureSwitch™ Multi-Volt Contactor is the next generation contactor with a microprocessor brain that replaces 24v, 120v, 208v, or 240v coil contactors.
Microprocessor control nearly eliminates contact welding and pitting
Sealed to keep out insects and debris
Protects condensers from brownouts and short cycling
Compatible with single stage residential AC/Heat pumps with PSC fan motors.
Also compatible with refrigeration equipment such as walk-in coolers, refrigeration cases, ice machines, and carbonated beverage machines.

## Slide 17: 49M11-843 SureSwitch™ Multi-Volt Contactor Features
Features:
Line voltage Brownout Protection
Test Button to simulate a 5 sec “Y” call
Short Cycle Protection Delay Switch
  - Factory set to on (3 minutes)
Lifetime Cycle count Button
Brown Out Protection Switch
  - Factory set to on (180v >4sec.)
Tricolor LED Fault/Status Indicator
24v/120v/240v Coils
Random Start Delay following Brownout (5-90sec.) (Not Pictured)
Sealed Contacts (Not Pictured)
49M11-843
4
2
3
1
5
8
6
7

## Slide 18: Easy Replacement
SureSwitch replaces 1, 1.5, or 2 pole contactors with the identical mounting footprint.
Four-hole mounting pattern matches industry standard contactors.
SureSwitch
Typical
Contactor
2-3/8” H
3-7/8” L
2-3/4” W

## Slide 19: Product Improvements of the 49M11-843 SureSwitch™ Multi-Volt Contactor
Coil voltage options of 24v, 120v, 208v,& 240v
  Refrigeration Compatible
  Red cap on 120/240v coil terminal
Removable Label to identify Switched and Non-Switched legs.
Brighter LED
  Higher visibility reading
Taller Dividers between Coil Spades
49M11-843
49P11-843

## Slide 20: Feature and Design
SureSwitch™ inside view two panel design
Stacked circuit board design helps keep product
dimensions as compact as possible
Product Benefit/Feature
User interface/coil board
Power supply
High voltage bottom PCB
Sealed relay switches compressor & fan loads
Inside the sealed relay box.
4
2
3
1

## Slide 21: FAQ
SureSwitch™ wiring flexibility ensures fit in
greatest number of applications.
Replaces 1,1.5, or 2 pole contactors up to 40 FLA
Covers a Majority of OEM use on new units
Run L1
UNSWITCHED
L2
SWITCHED
Comp Common
SWITCHED
Fan
SWITCHED
Design functions the same as a
contactor with shunt on one leg.
Flexibility to mount sideways as needed
to avoid over manipulating wiring.

## Slide 22: Coil Voltage Options
Applicable to 24v, 120v, 208v, or 240v coils, the SureSwitch is a reliable option for replacing refrigeration contactors. Determine the correct coil voltage by looking at the contactor being replaced.
SureSwitch comes with a red cap on one of the line voltage coil spade terminals. On line voltage applications, it can be moved to the 24V Y terminal.
The coil diagram shows how to connect line voltage or 24V coil wires. Only one coil should be connected
2
1

## Slide 23: Refrigeration Wiring Considerations
In refrigeration equipment, it's best to review the schematic and determine the switched and common lines. Typically, the switched line is labeled "L1" or "Line" and the common line is labeled "L2" or "Neutral".
The "L1" or "Line" input wire should be connected to the switched "LINE IN" lug, and the corresponding wire for the compressor should be connected to the switched "LOAD OUT" lug.
The "L2" or "Neutral" input wire should be connected to the common "LINE IN" lug, and the corresponding wire for the compressor should be connected to the commone "LOAD OUT" lug.
For refrigeration applications, brownout and short cycle delay switches should be set to "OFF".
2
1
1

## Slide 24: Tri-Color LED
Using the LED
The New LED indicator light has higher visibility to be seen easier in tighter installations
Press the “TEST” button for one second to energize the compressor and fan for five seconds to simulate a call for cooling.
The “TEST” button will also allow the short cycle time delay to be bypassed if a call for cooling is present, by pressing the “TEST” button for one second as well.
49M11-843

## Slide 25: Comparison to Older / Competitive Products
Brownout Protection
Shuts off the compressor and fan if line voltage is below 180VAC for more than 4 seconds
  Fast-flashing Green/Red LED lets you know if voltage is low
Operation resumes if line voltage returns to a minimum of 190VAC
SureSwitch will not attempt to start the compressor and fan if line voltage is less than 187 VAC
  Fast-flashing Green/Red LED lets you know if voltage is low
SureSwitch ships with this feature turned on, but can be switched off by dipswitch
1
Reduces chance for compressor and condenser fan motor damage; motor winding temps rise 10-15% for each 10% of voltage drop.
1
Brownout
Protection
49M11-843

## Slide 26: Comparison to Older / Competitive Products
Short Cycle Delay
SureSwitch starts a three-minute delay at power-up, and any time the compressor is shut down
  Fast-flashing green LED indicates a delay is present
SureSwitch ships with this feature turned on, but can be switched off by dipswitch
Rapid cycling can pump out oil and do damage to compressors.
If system pressures aren’t allowed enough time to equalize, motor windings can be stressed.
2
Short
Cycle Delay
2
49M11-843
1
Brownout
Protection
2
Short
Cycle Delay
+

## Slide 27: Comparison to Older / Competitive Products
Random Start Delay
SureSwitch starts a 5-90 second delay, at power-up and recovery from a brownout.
  Fast-flashing Green LED indicates a delay is present
Normal compressor cycling will not activate a Random Start Delay
3
Perfect for multi-unit installs like apartments to help reduce blackouts/brownouts from multiple loads restarting simultaneously.
3
Random
Start Delay
=
3
Random
Start Delay
49M11-843
1
Brownout
Protection
2
Short
Cycle Delay
+
+

## Slide 28: Specs
Recommended Terminal
Torque – L1, L2, T2(R) and T1(C)
#4–6AWG: 45in-lbs
#8AWG: 40in-lbs
#10–14AWG: 35in-lbs
24 VAC (Y,C) terminals are ¼” male QC’s accepting #12-24AWG wire
Terminal Designations
SureSwitch requires line voltage for operation and testing.
ELECTRICAL RATINGS
Line voltage input: 120/208/240 VAC, 1-phase, 50/60 Hz
Full load amperes: (FLA) 40A
Locked rotor amperes: (LRA) 200A
24 VAC Control (Coil) Voltage (Y,C): 24 VAC, 50/60 Hz
120/240 VAC Control (Coil) Voltage:
120/208/240 VAC, 1-phase, 50/60 Hz
For 2 Pole applications if local electrical codes are met
Operating Temperature Range
-40° to 158° F (-40° to 70°C)
Humidity Range
5 to 95% relative humidity (non-condensing)
Dimensions
2-3/4" W x 2-3/8" H x 3-7/8" L
Timings
Short-cycle delay: 0s or 180s (selectable) at 60 Hz 0s or 216s (selectable) at 50Hz
Compressor test: 5s at 60 Hz 6s at 60 Hz
Notes: 1-phase, 50/60 Hz

## Slide 29
Install
49M11-843 SureSwitch™ Multi-Volt Contactor

## Slide 30: Installing the SureSwitch Multi-Volt Contactor
The 49M11-843 SureSwitch™ Multi-Volt Contactor replaces 24v, 120v, 208v, or 240v coil contactors. And has wide compatibility with single stage residential AC/Heat pumps with PSC fan motors as well as refrigeration equipment such as walk-in coolers, refrigeration cases, ice machines, and carbonated beverage machines.
Today, we’ll walk through install steps for residential A/C or a heat pump.

## Slide 31: What’s in the Box
List of Contents:
SureSwitch™ Contactor
Instruction Sheet
Control Box Label
2x Mounting Screws
1x Dual Spade Splitter
SureSwitch™ Contactor Upgrade
UL Label

## Slide 32: 49M11-843 SureSwitch™ Multi-Volt Contactor Features
Features:
Line voltage Brownout Protection
Test Button to simulate a 5 sec “Y” call
Short Cycle Protection Delay Switch
  - Factory set to on (3 minutes)
Lifetime Cycle count Button
Brown Out Protection Switch
  - Factory set to on (180v >4sec.)
Tricolor LED Fault/Status Indicator
24v/120v/240v Coils
Random Start Delay following Brownout (5-90sec.) (Not Pictured)
Sealed Contacts (Not Pictured)
49M11-843
4
2
3
1
5
8
6
7

## Slide 33: Installation – Step 1
1
Turn off the power to the condensing unit
Disconnect the power coming from the indoor unit
Remove the access panels

## Slide 34: Installation – Step 2
2
Scan the QR on the package to download WR Mobile and check for the appropriate cross reference on the existing install.

## Slide 35: Installation – Step 3
3
Always a good idea to take a quick picture of the existing installation before disconnecting.

## Slide 36: Installation – Step 4
4
Remove the Wiring:
Remove 24v coil wires
Disconnect line voltage
Verify circuit on shunt leg
Remove yellow and black wires from shunt and switch sides
Note the locations of the wires as you remove them, particularly the black wire with red tape connected to the line in switched side.
Remove the contactor

## Slide 37: Installation – Step 5
5
Select flat mounting location and then separate the housing, noting the base orientation before separating. You'll note that three screws are loose, and one is tightened when it comes from the factory.

## Slide 38: Installation – Step 6
6
Attach mounting base to the control panel and then reattach the SureSwitch™ to the base with 4 included screws.

## Slide 39: Installation – Step 7
7
Connect the wiring:
Remove label over contacts before beginning
Attach line voltage to L1 and L2, torque to spec
Install common and run wires, removing connectors if necessary, to T1 and T2, torque to spec
  Yellow is T1 / Black is T2
  Install remaining yellow wires to T1 shunt leg
Attach black wire with red tape to L2
  Install remaining black wires to T2
Based on application, utilize spade terminals
  (Here, 24v wires to Y and C, red cap stays on line spade terminal)

## Slide 40: Installation – Step 8
8
For short cycle time delay and brownout protection, dipswitches are factory set to “on”. If desired, disable with a small screwdriver.

## Slide 41: Installation – Step 9
9
Test your work:
Turn on the power to the condensing unit
Turn on the low voltage from the indoor unit
  Green LED will flash slow indicating stand-by mode

## Slide 42: Installation – Step 10
Test your work:
Press the test button for one second to enter self-test mode.
Initiate a call for cooling
  Rapid Green LED flash = short cycle delay
Bypass short cycle delay by pressing Test for 1 second
  Solid Green LED = normal operation
Terminate call for cooling
10

## Slide 43: Installation – Step 11
Lifetime Cycle Count
Press the count button for one second to view the total number of compressor cycles.
If desired, reset the cycle count by pressing Test and Count for 2 seconds. LED will flash red and yellow.
11

## Slide 44: Installation – Step 12
Apply the control label inside the control box, reattach the access panel and you’re good to go.
12

## Slide 45
Thank You
49M11-843 SureSwitch™ Multi-Volt Contactor